## Rectangular Wier 1 (hidden)
This is for calculating flow on The Type of Weir as pictured
This works best for flow over a Bascule Gate (SWO Gate)
ONLY TYPE IN RED SQUARES
Click here to Pick Units FIRST;
Water Depth = | 2 | Feet
Depth
Length of Weir = | 60 | Feet
Flow = | 365.2065 | MGD
Weir Formula = | 2.152 x L x H^1.5
|  |  |  | H | L
|  |  |  | 2 | 60
|  |  | 2.152 | 60 | 2.8284 | GPM | Inches
[6 empty] | MGD | Feet
Ft3/sec.
(no end contractions)
Length

## Rectangular Wier 2 (hidden)
This is for calculating flow on The Type of Weir as pictured
THIS WILL WORK BEST FOR A SIDESPILL WEIR
ONLY TYPE IN RED SQUARES
Click here to Pick Units;
Water Depth (H max.) = | 2 | Feet
Length of Weir (L) = | 5 | Feet
Flow = | 43.3258 | Ft3/sec.
Weir Formula = | 3.330(L-.2H)H^1.5
|  |  |  | H | L
|  |  |  | 2 | 5
|  |  | 3.33 | 4.6 | 2.8284 | GPM | Inches
[6 empty] | MGD | Feet
Ft3/sec.
(with end contractions)
2Hmax. Minimum
Hmax.
2Hmax. Minimum
L = Crest Length

## Round Outfall Pipe
This method is for use in situations as pictured. For use in generally smaller pipes.
As pipes approach 3 feet in diameter, this method begins to lose accuracy.
WWW.SEWERGEEK.COM
ONLY TYPE IN RED SQUARES
| Click here to Pick Units; | [5 empty] | 6D Minimum
Water Depth (H) = | 6.25 | Inches |  |  |  |  | D
H
Pipe Diameter (D) = | 4.33 | Feet
Flow must free fall.
Flow = | 11.0383 | Ft3/sec. |  |  |  |  | Pipe must be very close to flat.
Accuracy diminishes as as slopes increase
Formula; Q = | 8.69[1-(D-H)/D]^1.88 x D^2.88
If the velocity and depth are known, use a different worksheet called "Sewer Flows with grit.xls"
|  |  |  | H | D
|  |  |  | 0.52083 | 4.33
|  |  | 8.69 | 0.12028 | 0.018655 | 68.0903 | GPM | Inches
|  |  | Constant | [1-(D-H)/D] | ^1.88 | D^2.88 | MGD | Feet
Ft3/sec.
(California Pipe Method)

## Flows with Grit (hidden)
ONLY TYPE IN RED SQUARES | [5 empty] | Inches
(Grit levels can be zero) | [5 empty] | Feet
Round Pipe |  |  |  | Dropdown menus
Pipe Dia. |  | 60 | Inches | 5
Depth |  | 3 | Feet | 3
Grit |  | 11 | Inches | 0.91667 | Dia.
Avg. Vel. |  | 2 | ft/sec. | 2 |  | Depth
Grit
MGD | = | 12.795
CFS | = | 19.8323 |  | 12.2416
GPM | = | 8900.7138 |  | 0.080881
0.6 |  | 0.318 |  |  | 0.18333 | 0.0621
L/D |  | MGD |  |  | Full pipe flow = | 15.9
0.01 | = | 0.0009 | 0.001395 |  | Equivelant flow from grit = | 3.105
0.02 | = | 0.0024 | 0.00372 |  | Balance = | 12.795
0.03 | = | 0.0044 | 0.00682
0.04 | = | 0.0068 | 0.01054
0.05 | = | 0.0095 | 0.014725
0.06 | = | 0.0124 | 0.01922
0.07 | = | 0.0156 | 0.02418
0.08 | = | 0.019 | 0.02945
0.09 | = | 0.0226 | 0.03503
0.1 | = | 0.0264 | 0.04092
0.11 | = | 0.0304 | 0.04712
0.12 | = | 0.0345 | 0.053475
0.13 | = | 0.0388 | 0.06014
0.14 | = | 0.0432 | 0.06696
0.15 | = | 0.0477 | 0.073935
0.16 | = | 0.0524 | 0.08122
0.17 | = | 0.0572 | 0.08866
0.18 | = | 0.0621 | 0.096255
0.19 | = | 0.0672 | 0.10416
0.2 | = | 0.0723 | 0.11207
0.21 | = | 0.0775 | 0.12012
0.22 | = | 0.0828 | 0.12834
0.23 | = | 0.0882 | 0.13671
0.24 | = | 0.0937 | 0.14524
0.25 | = | 0.0992 | 0.15376
0
0.26 | = | 0.1049 | 0.16259
0.27 | = | 0.1106 | 0.17143
0.28 | = | 0.1163 | 0.18027
0.29 | = | 0.1222 | 0.18941
0.3 | = | 0.1281 | 0.19855
0.31 | = | 0.134 | 0.2077
0.32 | = | 0.14 | 0.217
0.33 | = | 0.1461 | 0.22646
0.34 | = | 0.1522 | 0.23591
0.35 | = | 0.1583 | 0.24536
0.36 | = | 0.1645 | 0.25498
0.37 | = | 0.1707 | 0.26459
0.38 | = | 0.177 | 0.27435
0.39 | = | 0.1833 | 0.28412
0.4 | = | 0.1896 | 0.29388
0.41 | = | 0.196 | 0.3038
0.42 | = | 0.2023 | 0.31357
0.43 | = | 0.2087 | 0.32349
0.44 | = | 0.2151 | 0.33341
0.45 | = | 0.2215 | 0.34332
0.46 | = | 0.228 | 0.3534
0.47 | = | 0.2344 | 0.36332
0.48 | = | 0.2409 | 0.3734
0.49 | = | 0.2473 | 0.38332
0.5 | = | 0.2538 | 0.39339
0.51 | = | 0.2603 | 0.40346
0.52 | = | 0.2667 | 0.41339
0.53 | = | 0.2732 | 0.42346
0.54 | = | 0.2796 | 0.43338
0.55 | = | 0.2861 | 0.44346
0.56 | = | 0.2925 | 0.45337
0.57 | = | 0.2989 | 0.4633
0.58 | = | 0.3053 | 0.47322
0.59 | = | 0.3117 | 0.48313
0.6 | = | 0.318 | 0.4929
0.61 | = | 0.3243 | 0.50267
0.62 | = | 0.3306 | 0.51243
0.63 | = | 0.3369 | 0.52219
0.64 | = | 0.3431 | 0.53181
0.65 | = | 0.3493 | 0.54141
0.66 | = | 0.3554 | 0.55087
0.67 | = | 0.3615 | 0.56032
0.68 | = | 0.3676 | 0.56978
0.69 | = | 0.3736 | 0.57908
0.7 | = | 0.3795 | 0.58822
0.71 | = | 0.3854 | 0.59737
0.72 | = | 0.3913 | 0.60652
0.73 | = | 0.397 | 0.61535
0.74 | = | 0.4027 | 0.62418
0.75 | = | 0.4084 | 0.63302
0.76 | = | 0.4139 | 0.64155
0.77 | = | 0.4194 | 0.65007
0.78 | = | 0.4248 | 0.65844
0.79 | = | 0.4301 | 0.66665
0.8 | = | 0.4353 | 0.67472
0.81 | = | 0.4405 | 0.68278
0.82 | = | 0.4455 | 0.69053
0.83 | = | 0.4505 | 0.69828
0.84 | = | 0.4552 | 0.70556
0.85 | = | 0.4599 | 0.71284
0.86 | = | 0.4644 | 0.71982
0.87 | = | 0.4688 | 0.72664
0.88 | = | 0.4731 | 0.73331
0.89 | = | 0.4772 | 0.73966
0.9 | = | 0.4812 | 0.74586
0.91 | = | 0.485 | 0.75175
0.92 | = | 0.4886 | 0.75733
0.93 | = | 0.492 | 0.7626
0.94 | = | 0.4952 | 0.76756
0.95 | = | 0.4981 | 0.77206
0.96 | = | 0.5008 | 0.77624
0.97 | = | 0.5032 | 0.77996
0.98 | = | 0.5052 | 0.78306
0.99 | = | 0.5068 | 0.78554
1 | = | 0.5076 | 0.78678